## Sheet2
1.4GW ESS 현황
년도 | 변전소 | 용량 | PMS | PCS | BAT
| 신남원 | 336(168)
| 함양 | 56
| 영주 | 56 | 네오피스 | LS일렉트릭 | 삼성SDI
| 부북 | 336
| 영천 | 112
| 예산 | 82

## Ver_Manage
Version 관리
Ver | 내용 | 담당자 | 변경일자 | 비고
1.6 | 1. SOC - SOH_IR 축약 로직 추가 - 통신 차단 (예: CV<2V) 시 SOC 변경 홀딩 : SOCstate =-1로 표기 2. SOH_C - SOC_Range 추가(output_13) : 하루단위 Max/Min SOC 범위 정보 추가 | 선임 이성은 | 2021.04.30
1.7 | 1.Sox 통합 - SOC, SOH_C, SOH_P, POL 2. SOH_C - Temp_Range추가(output_14) : 하루단위 Max of MaxTemp/Max of AvgTemp 3. SOX_CellM 추가 - 22Cell/Module 기준 적용 | 선임 이성은 | 2021.08.09
1.8 | 1.Sox Input 추가 - DC power, Reset(Pre_SOH), modbus SOC,SOH | 선임 이성은 | 2021.10.08
1.9 | 1.이름변경 - SOS -> SOT | 선임 이성은 | 2021.10.19
1.10 | 1.SOHC '-input : Reset 추가 | 선임 이성은 | 2021.12.21
1.11 | 1.SOT - SOC Range -> Max, Min 으로 분리 - Temp Range -> Max, Min으로 분리 | 선임 이성은 | 2022.1.10
1.12 | 1.이름변경 - SOHC -> SOXC : 모듈 단위 셀 SOX 파일 2. 추가 `- SOXCR : Rack 단위 모든 셀 SOX 파일 | 선임 이성은 | 2022.1.23
1.13 | 1. 추가 '- SOX(input 15) : SOH_T(SOT의 추정 SOH값) '- SOX(Output 2) : Timer_inner
1.14 | 1.변경 `- SOXC : 입출력 재정의( 입력:776, 출력:1496) 2. 추가 '- SOX(Output 25~28) : 세부 IR 연산(HV, LV) | 선임 이성은 | 2022.3.7
1.15 | 1.변경 `- SOXC : 입출력 재정의( 입력:776, 출력:1871) | 선임 이성은 | 2022.3.8
1.16 | 1.변경 `- SOXC : SOH_C 일부 스케일 변경 0.1 -> 0.01 | 선임 이성은 | 2022.3.21
1.17 | 1.변경 `- SOX,SOT : HMI 표기 데이터 정리 | 선임 이성은 | 2022.4.4
1.18 | 1. 추가 '- SOXC(Output) : Min, Max, Avg SOC_C, SOH_C, SOH_P | 선임 이성은 | 2022.4.14
1.19 | 1. 변경 '- Reserve_Input_4 => Stored_SOH_P | 선임 이성은 | 2022.7.11

## Q&A
구분 | 날짜 | 질문 | 답변 | 답변자
1 | 21.10.17 | DLL의 Reserve 영역에 추가(상수, 통신값 등)시 변경 절차 문의 - Labview에서 간단하게 추가 가능한지?
2 | 21.10.17 | DLL의 Ourput에 문자 표기(Version)도 가능한지? - 예) 220301_GMAK
3 | 21.10.17 | DLL 업데이트시 쉽고 간략하게 업데이트 하는 방법?

## SOX(SOC,SOH)
SOX
| Sampling Time : |  | 100ms (Monitoring : 1s)
INPUT
No. | Name | Type | Description | Data Type | Unit | Range | Resolution | Comment (Initial Value) | Commercial (HMI)
1 | DC_Current | Modbus | Value of Measured Pack(Module) Current | int16 | A | -300~300 | 0.01 |  | O
2 | DC_Power | Modbus | DC Power of Rack(kW) | int16 | kW | 1~100000 | 0.01 |  | O
3 | CV_Avg | Modbus | Value of measured average cell voltage | uint16 | V | 0~5 | 0.001 |  | O
4 | CV_Max | Modbus | Value of measured max cell voltage | uint16 | V | 0~5 | 0.001 |  | O
5 | CV_Min | Modbus | Value of measured min cell voltage | uint16 | V | 0~5 | 0.001 |  | O
6 | MT_Avg | Modbus | Value of measured Average temperature | int16 | degC | -40~100 | 0.01 |  | O
7 | MT_Max | Modbus | Value of measured max temperature | int16 | degC | -40~100 | 0.01 |  | O
8 | MT_Min | Modbus | Value of measured mintemperature | int16 | degC | -40~100 | 0.01 | (300) | O
9 | Restart_Time | Internal System | Value of restart time from final shut down
10 | Stored_SOC | Parameter(Data file) | Final SOC value | uint16 | % | 0~100 | 0.01 | Last SOC value in Data folder (100)
11 | Stored_SOH | Parameter(MNTR file) | Final SOH_C value | uint16 | % | 0~100 | 0.01 | Last SOH_C value in MNTR folder (100)
12 | Modbus_SOC | Modbus | BMS SOC by Modbus comm. | uint16 | % | 0~100 | 0.01 |  | O
13 | Modbus_SOH | Modbus | BMS SOH by Modbus comm. | uint16 | % | 0~100 | 0.01 |  | O
14 | Reset_SOH_C | Commend in HMI | Reset SOH_C pre value |  |  |  |  | Last SOH_C value in MNTR folder (100)
15 | Dev_SOH | SOT(Dev_SOH,Out29) | SOH of SOT Logic | uint16 | % | 0~100 | 0.01
16 | Stored_SOH_P | Parameter(MNTR file) | Final SOH_C value | uint16 | % | 0~100 | 0.01 | Last SOH_C value in MNTR folder (100)
17 | Reserve_Input_3
18 | Reserve_Input_2
19 | Reserve_Input_1
20 | LPMS_Mode | Modbus | LPMS_FRC_Mode | uint16 |  | 0~1000 | 1
OUTPUT
No. | Name |  | Description | Data Type | Unit | Range | Resolution | Comment | Commercial (HMI) | Commercial
[10 empty] | (Stored every second) | (Stored one per day)
1 | SOX_Ver |  | Date ex:200329001 | uint16 | % | 1~20999999 | 1 |  |  |  | O
2 | Flag |  | state
3 | Reserve_Out_10
4 | Final_SOC |  | Average_SOC | uint16 | % | 0~100 | 0.01 | SOC | O | O
5 | Upper_SOC |  | Upper SOC | uint16 | % | 0~100 | 0.01 | SOC | O | O
6 | Low_SOC |  | Low SOC | uint16 | % | 0~100 | 0.01 | SOC | O | O
7 | SOCv |  | SOCv | uint16 | % | 0~100 | 0.01 | SOC |  | O
8 | SOC_State |  | 0:stable, 1: stop, 2:run, -1:Com Disconnect | uint32 | state | 0~10 | 1 | SOC |  | O
9 | ChrDchr_Check |  | -1:Dchr, 0: middle, 1:Chr | uint32 | state | 0~10 | 1 | SOC |  | O
10 | Timer_inner |  | Timer For Check State | uint32 | Min | 0~100 | 0.01 | SOC |  | O
11 | Reserve_Out_9
12 | SOH_C |  | SOH inner value | uint16 | % | 1~100 | 0.01 | SOH_C | O | O | O
13 | DOD |  | Depth of Discharge | uint16 | % | 1~1000 | 0.01 | SOH_C |  | O | O
14 | Accum_Ah |  | Accumulation of Ah | uint16 | % | 1~100 | 0.1 | SOH_C([-]Dchr SOH_Ah) |  | O | O
15 | SOH_Ah |  | Calculation of SOH based on Ah | uint16 | % | 1~100 | 0.01 | SOH_C(Ah) |  | O | O
16 | Accum_Wh |  | Accumulation of Wh | uint16 | % | 1~100 | 0.1 | SOH_C([-]Dchr SOH_Wh) |  | O | O
17 | SOH_Wh |  | Calculation of SOH based on Wh | uint16 | % | 1~100 | 0.01 | SOH_C(Wh) |  | O | O
18 | Timer_IR |  | Timer For IR Calc | uint32 | Sec | 0~100 | 0.01 |  |  | O
19 | IR_Calc |  | SOH_IR inner value | uint16 | % | 0~10 | 0.001 | SOH_P |  | O | O
20 | IR_Chr |  | IR of Charge | uint16 | % | 0~10 | 0.001 | SOH_P |  | O | O
21 | IR_DChr |  | IR of Discharge | uint16 | % | 0~10 | 0.001 | SOH_P |  | O | O
22 | IR_Chr_Dev |  | Deviation of IR Charge | uint16 | % | 0~10 | 0.001 | SOH_P |  | O | O
23 | IR_DChr_Dev |  | Deviation of IR Discharge | uint16 | % | 0~10 | 0.001 | SOH_P |  | O | O
24 | SOH_P |  | Incresing rate of IR | uint16 | % | 0~1000 | 0.1 | SOH_P | O | O | O
25 | IR_LV_Chr |  | IR of Low V in Charge | uint16 | % | 0~10 | 0.001 |  |  | O | O
26 | IR_LV_DChr |  | IR of Low V in Discharge | uint16 | % | 0~10 | 0.001 |  |  | O | O
27 | IR_HV_Chr |  | IR of High V in Charge | uint16 | % | 0~10 | 0.001 |  |  | O | O
28 | IR_HV_DChr |  | IR of High V in Discharge | uint16 | % | 0~10 | 0.001 |  |  | O | O
29 | Chr_Pwr_Limit |  | Charge Power Limit | uint16 | kW | 0~300 | 0.1 | POL |  | O
30 | DChr_Pwr_Limit |  | DisCharge Power Limit | uint16 | kW | 0~300 | 0.1 | POL |  | O
31 | Chr_Crr_Limit |  | Charge Current Limit | uint16 | A | 0~300 | 0.1 | POL |  | O
32 | DChr_Crr_Limit |  | DisCharge Current Limit | uint16 | A | 0~300 | 0.1 | POL |  | O
33 | Reserve_Out_8 | [9 empty] | O
34 | Reserve_Out_7 | [9 empty] | O
35 | Reserve_Out_6 | [9 empty] | O
36 | Reserve_Out_5 | [9 empty] | O
37 | Reserve_Out_4 | [8 empty] | O
38 | Reserve_Out_3 | [8 empty] | O
39 | Reserve_Out_2 | [8 empty] | O
40 | Reserve_Out_1 | [8 empty] | O

## SOXC
SOX_Cell
| Sampling Time : |  | 100ms (Monitoring : 1s)
INPUT
No. | Name | Type | Description | Data Type | Unit | Range | Resolution | Comment (Initial Value)
1 | Reset | System Clock | Function Reset ( init : 0 -> 1 -> 0[restart])
2 | DC_Current |  | Value of Measured Pack(Module) Current | int16 | A | -300~300 | 0.01
3 | Stored_SOC | Parameter(DATA file) | Final SOC value | uint16 | % | 0~100 | 0.01
4 | Reserve_Input_25
…
27 | Reserve_Input_2
28 | Reserve_Input_1
29 | Cell_V_1_1 |  | CV_M1C1 | uint16 | V | 0~5 | 0.001
30 | Cell_V_1_2 |  | CV_M1C2 | uint16 | V | 0~5 | 0.001
… | …
50 | Cell_V_1_22 |  | CV_M1C22 | uint16 | V | 0~5 | 0.001
51 | Cell_V_2_1 |  | CV_M2C1
…
402 | Cell_V_17_22
403 | SOHC_1_1 |  | Final SOH value | uint16 | % | 0~100 | 0.01 | (ini : 100, next :SOH_C_M1C1[Stored Data])
404 | SOHC_1_2 |  | Final SOH value | uint16 | % | 0~100 | 0.01 | (ini : 100, next :SOH_C_M1C2[Stored Data])
… | …
424 | SOHC_1_22 |  | Final SOH value | uint16 | % | 0~100 | 0.01 | (ini : 100, next :SOH_C_M1C22[Stored Data])
425 | SOHC_2_1
…
776 | SOHC_17_22 |  | Final SOH value | uint16 | % | 0~100 | 0.01
OUTPUT
No. | Name |  | Description | Data Type | Unit | Range | Resolution | Comment | Commercial (HMI) | Commercial (Stored one per day)
1 | SOXC_Ver |  | Date ex:220126 | uint16 | % | 1~20999999 | 1 |  | O
2 | Avg_SOC_C
3 | Max_SOC_C
4 | Min_SOC_C
5 | Avg_SOH_C
6 | Max_SOH_C
7 | Min_SOH_C
8 | Avg_SOH_P
9 | Max_SOH_P
10 | Min_SOH_P
11 | Reserved_10
12 | Reserved_9
13 | Reserved_8
14 | Reserved_7
15 | Reserved_6
16 | Reserved_5
17 | Reserved_4
18 | Reserved_3
19 | Reserved_2
20 | Reserved_1
21 | O_SOC_1_1 |  | SOC(Module1 - Cell1) | uint16 | % | 0~100 | 0.01 | SOC
22 | O_SOC_1_2 |  | SOC(Module1 - Cell2) | uint16 | % | 0~100 | 0.01 | SOC
… | …
42 | O_SOC_1_22 |  | SOC(Module1 - Cell22) | uint16 | % | 0~100 | 0.01 | SOC
43 | O_SOC_2_1 |  | SOC(Module2- Cell1)
… | …
394 | O_SOC_17_22 |  | SOC(Module17- Cell22) | uint16 | % | 0~100 | 0.01 | SOC
395 | O_SOHC_1_1 |  | SOHC(Module1 - Cell1) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
396 | O_SOHC_1_2 |  | SOHC(Module1 - Cell2) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
…
416 | O_SOHC_1_22 |  | SOHC(Module1 - Cell22) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
417 | O_SOHC_2_1 |  | SOHC(Module2 - Cell1) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
…
768 | O_SOHC_17_22 |  | SOHC(Module17 - Cell22) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
769 | O_SOHP_1_1 |  | SOHP(Module1 - Cell1) | uint16 | % | 0~100 | 0.01 | SOH_P(Stored Value) |  | O
770 | O_SOHP_1_2 |  | SOHP(Module1 - Cell2) | uint16 | % | 0~100 | 0.01 | SOH_P(Stored Value) |  | O
…
790 | O_SOHP_1_22 |  | SOHP(Module1 - Cell22) | uint16 | % | 0~100 | 0.01 | SOH_P(Stored Value) |  | O
791 | O_SOHP_2_1 |  | SOHP(Module2 - Cell1) | uint16 | % | 0~100 | 0.01
1142 | O_SOHP_17_22 |  | SOHP(Module17 - Cell22) | uint16 | % | 0~100 | 0.01
1143 | O_SO_1_1 |  | SO(Module1 - Cell1) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
1144 | O_SO_1_2 |  | SO(Module1 - Cell2) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
…
1164 | O_SO_1_22 |  | SO(Module1 - Cell22) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
1165 | O_SO_2_1 |  | SO(Module2 - Cell1) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
…
1516 | O_SO_17_22 |  | SO(Module17 - Cell22) | uint16 | % | 0~100 | 0.01 | SOH_C(Stored Value) |  | O
1517 | O_S_1_1 |  | S(Module1 - Cell1) | uint16 | % | 0~100 | 0.01 | SOH_P(Stored Value) |  | O
1518 | O_S_1_2 |  | S(Module1 - Cell2) | uint16 | % | 0~100 | 0.01 | SOH_P(Stored Value) |  | O
…
1538 | O_S_1_22 |  | S(Module1 - Cell22) | uint16 | % | 0~100 | 0.01 | SOH_P(Stored Value) |  | O
1539 | O_S_2_1 |  | S(Module2 - Cell1) | uint16 | % | 0~100 | 0.01
1890 | O_S_17_22 |  | S(Module17 - Cell22) | uint16 | % | 0~100 | 0.01

## SOT
SOT(State of sTress Index)
| Sampling Time : |  | 1000ms
INPUT
No. | Name | Type | Description | Data Type | Unit | Range | Resolution | Comment (Initial Value) | Commercial (HMI) | SDI(금악)
1 | DC_Current | Modbus | Measured Pack(Module) Current(or Power) Value | int16 | A | -300~300 | 0.01 |  | O
2 | CV_Avg | Modbus | Average value of measured cell voltage values | uint16 | V | 0~5 | 0.001 |  | O
3 | CV_Max | Modbus | Max value of measured cell voltage values | uint16 | V | 0~5 | 0.001 |  | O
4 | CV_Min | Modbus | Min value of measured cell voltage values | uint16 | V | 0~5 | 0.001 |  | O
5 | MT_Avg | Modbus | Average value of measured temperature values | int16 | degC | -40~100 | 0.01 |  | O
6 | MT_Max | Modbus | Max value of measured temperature values | int16 | degC | -40~100 | 0.01 |  | O
7 | MT_Min | Modbus | Min value of measured temperature values | int16 | degC | -40~100 | 0.01 |  | O |  |  | Value |  | SPH_Dev |  | SPH_Max |  | SPD_Dev |  | SPD_Max |  | SPC_Max
8 | SOC | SOX(SOC) | Final SOC value | uint16 | % | 0~100 | 0.01 |  |  |  |  | 1 | 주의 | 0.5 | 0.3 | 1 | 0.8 | 0.5 | 0.3 | 1 | 0.8 | 1 | 0.9
9 | Rack_Num | Parameter(Constant) | Total Rack Number | uint16 | EA | 1~100000 | 1 | (4MW Based) |  | 38 |  | 2 | 알람 | 0.8 | 0.6 | 4 | 2 | 0.8 | 0.6 | 4 | 2 | 1.5 | 1.4
10 | Cell_Num | Parameter(Constant) | Total Cell Number | uint16 | EA | 1~100000 | 1 | (1Rack Based) |  | 264 |  | 3 | 경고 | 1 | 0.9 | 6 | 5 | 1 | 0.9 | 6 | 5 | 2 | 1.9
11 | C_Rate | Parameter(Constant) | Battery C_rate in ESS | uint16 | C | 0.2~4 | 0.1 | (if 4C -> 4, 1C->1) |  | 1 |  | 4 | 위험 | 1.3 | 1.1 | 8 | 7 | 1.3 | 1.1 | 8 | 7 | 2.5 | 2.4
12 | Init_Cap | Parameter(Constant) | Battery Capacity | uint16 | Ah | 0~200 | 1 | (Cell Ah) |  | 112
13 | Stored_SOH | SOX(SOH_C) | Final SOH value | uint16 | % | 0~100 | 0.1 | Last SOH_C value in MNTR folder (100) | [5 empty] | Case_Study | [9 empty] | 설명
14 | Reset | System Clock | Function Reset ( init : 0 -> 1 -> 0[restart]) |  |  | 0,1 | 1 | (0) | [5 empty] | 2 |  | 1 |  | 1 |  | 1 |  | 1 |  | 순간 정격 충방전 동작 가능성 높음
15 | Max_CV_M_Num | Modbus | Max_CV_Module_Num | uint16 |  | 0~100 | 1 | [6 empty] | 1 |  | 1 |  | 1 |  | 2 |  | 1 |  | 누적 충방전양이 많을 가능성 높음
16 | Max_CV_C_Num | Modbus | Max_CV_Cell_Num | uint16 |  | 0~100 | 1 | [6 empty] | 1 |  | 2 |  | 1 |  | 2 |  | 1 |  | 누적 충방전양이 많을 가능성 높음
17 | Min_CV_M_Num | Modbus | Min_CV_Module_Num | uint16 |  | 0~100 | 1
18 | Min_CV_C_Num | Modbus | Min_CV_Cell_Num | uint16 |  | 0~100 | 1
19 | Max_MT_M_Num | Modbus | Max_MT_Module_Num | uint16 |  | 0~100 | 1 | [6 empty] | 2 |  | 1 |  | 2 |  | 1 |  | 1 |  | 특정 셀 또는 모듈 열화 의심(충전시 최대 전압, 온도 모듈 동일 시, 점검 요)
20 | Max_MT_S_Num | Modbus | Max_MT_Sensor_Num | uint16 |  | 0~100 | 1 | [6 empty] | 2 |  | 2 |  | 2 |  | 2 |  | 2 |  | 특정 셀 또는 모듈 열화 의심(충전시 최대 전압, 온도 모듈 동일 시, 점검 요)
21 | Location_#1 | ACPD | ACPD_Diag_Position of Upper Level2(M*100+C) | uint16 |  | 0~9999 | 1 | [6 empty] | 3 |  | 1 | [7 empty] | 특정 셀 또는 모듈 열화 의심(충전시 최대 전압, 온도 모듈 동일 시, 점검 요)
22 | Location_#2 | ACPD | ACPD_Diag_Position of Upper Level2(M*100+C) | uint16 |  | 0~9999 | 1 | [6 empty] | 3 |  | 2 |  | 2 |  | 2 |  | 2 |  | 특정 셀 또는 모듈 열화 의심(충전시 최대 전압, 온도 모듈 동일 시, 점검 요)
23 | Location_#3 | ACPD | ACPD_Diag_Position of Upper Level2(M*100+C) | uint16 |  | 0~9999 | 1
24 | Reserve_Input_2
25 | Reserve_Input_1
OUTPUT
No. | Name |  | Description | Data Type | Unit | Range | Resolution | Comment | Commercial (HMI) | Commercial
[10 empty] | (Stored every second) | (Stored one per day)
1 | SOT_Ver |  | Date ex:20200329 | uint16 | % | 1~100000 | 1
2 | SOH_T |  | Estimated SOH | uint16 | % | 0~100 | 0.01
3 | SPD |  | Stress index Per Day | uint16 |  | 0~100 | 0.01 |  | O |  | O
4 | SPD_Max |  | Max Stress index Per Day | uint16 |  | 0~100 | 0.01 |  | O |  | O
5 | SPD_Dev |  | Deviation of SPD | uint16 |  | 0~100 | 0.01 |  | O |  | O
6 | SPH |  | Stress index Per Hour | uint16 |  | 0~100 | 0.01 |  | O |  | O
7 | SPH_Max |  | Max Stress index Per Hour | uint16 |  | 0~100 | 0.01 |  | O | O
8 | SPH_Dev |  | Deviation of SPH | uint16 |  | 0~100 | 0.01 |  | O | O
9 | SPC |  | SPD Level Per Cycle | uint16 |  | 0~100 | 0.01 |  |  |  | O
10 | SPC_Max |  | SPD_Max Level Per Cycle | uint16 |  | 0~100 | 0.01 |  |  |  | O
11 | SPC_Dev |  | Deviation of SPC | uint16 |  | 0~100 | 0.01 |  |  |  | O
12 | CPD |  | Cycle Ah Per Day | uint16 | Ah |  | 0.1 |  | O |  | O
13 | Reset_Feed |  | Reset Feedback |  |  | 0,1 | 1
14 | Pre_SPH_Max |  | Maximum Value of SPH_Max per Day | [5 empty] | O |  | O
15 | SOC_Dev |  | Deviation of SOC Range (MaxSOC - Min_SOC) | uint16 |  | 1~9999 | 0.1 |  | O |  | O
16 | Temp_Dev |  | Deviation of Range (MaxTemp - AvgTemp) | uint16 |  | 1~9999 | 0.1 |  | O |  | O
17 | SOC_Max |  | Max SOC per Day | uint16 |  | 1~9999 | 0.1 |  | O |  | O
18 | SOC_Min |  | Min SOC per Day | uint16 |  | 1~9999 | 0.1 |  | O |  | O
19 | Temp_Max |  | Max of MaxTemp | uint16 |  | 1~9999 | 0.1 |  | O |  | O
20 | Temp_Avg |  | Max of AvgTemp | uint16 |  | 1~9999 | 0.1 |  | O |  | O
21 | Diagnosis_SOT |  | Diagnosis Result of SOT | uint16 |  | 1~100000 | 1 |  |  | O
22 | SPH_Dev_Diag |  | Stress index Per Hour | uint16 | % | 0~100 | 1 |  |  | O
23 | SPH_Max_Diag |  | Max Stress index Per Hour | uint16 |  | 0~100 | 1 |  |  | O
24 | SPD_Dev_Diag |  | Max Stress index Per Day | uint16 |  | 0~100 | 1 |  |  | O
25 | SPD_Max_Diag |  | Max Stress index Per Day | uint16 |  | 0~100 | 1 |  |  | O
26 | SPC_Max_Diag |  | Max SPD Per Cycle | uint16 |  | 0~100 | 1 |  |  | O
27 | Location_Check |  | Checking between ACPD and SOS | [6 empty] | O
28 | Dev_SOH | [9 empty] | O
29 | Reserve_Out_12 | [9 empty] | O
30 | Reserve_Out_11 | [9 empty] | O
31 | Reserve_Out_10 | [9 empty] | O
32 | Reserve_Out_9 | [9 empty] | O
33 | Reserve_Out_8 | [9 empty] | O
34 | Reserve_Out_7 | [9 empty] | O
35 | Reserve_Out_6 | [9 empty] | O
36 | Reserve_Out_5 | [8 empty] | O
37 | Reserve_Out_4 | [8 empty] | O
38 | Reserve_Out_3 | [8 empty] | O
39 | Reserve_Out_2 | [8 empty] | O
40 | Reserve_Out_1 | [8 empty] | O

## FR_SOH
Sampling Time : | not Determine(Default 1000ms)
INPUT
Name | Description | Data Type | Unit | Range | Resolution | Ini_Value
Freq | Grid Freq | uint16 | % | 0~100 | 0.0001
SampleT | Time Step | uint16 | % | 0~100 | 0.0001 | 1
E_rated | Battery Capacity(kWh) based 4000kW PCS |  | kWh |  |  | 1400
MTvalue | Temperature of Battery Module |  | C |  |  | 25
Standard_f |  |  | Constant |  |  | 60
Charge_Droop |  |  | Constant |  |  | 0.00279
Discharge_Droop |  |  | Constant |  |  | 0.00279
Frq_DeadBand_on |  |  | Constant |  |  | 0.03
Frq_DeadBand_off |  |  | Constant |  |  | 0.029
Frq_DeadBand_Rcv_on |  |  | Constant |  |  | 0.028
Frq_DeadBand_Rcv_off |  |  | Constant |  |  | 0.029
SOC_DeadBand |  |  | % |  |  | 2
SOC_DeadBandEnd |  |  | % |  |  | 1
Init_SOC |  |  | % |  |  | 65
Init_SOH |  |  | % |  |  | 100
CenterSOC |  |  | % |  |  | 65
UpLimitSOC |  |  | % |  |  | 90
LowLimitSOC |  |  | % |  |  | 10
UpLimitNormalSOC |  |  | % |  |  | 80
LowLimitNormalSOC |  |  | % |  |  | 50
RecoverPowerRate1 |  |  | % |  |  | 0.1
RecoverPowerRate2 |  |  | % |  |  | 0.15
Chg_effi |  |  | % |  |  | 0.95
DChg_effi |  |  | % |  |  | 1.05
Offset_Curr |  |  | A |  |  | -20
OUTPUT
Name | Description | Data Type | Unit | Range | Resolution
FR_Power | Power[kW] | uint16 | % | 0~100 | 0.01
FR_Mode | FR Mode | uint16 | % | 0~500 | 1
SOC
SOH_Simul
SPD
SPH
Analysis_Data_Bus
Version

## FR
Sampling Time : | 20ms
INPUT
Name | Description | Data Type | Unit | Range | Resolution
Frequency | Grid Freq | uint16 | % | 0~100 | 0.0001
SOC | Final SOC value | uint16 | % | 0~100 | 0.0001
OUTPUT
Name | Description | Data Type | Unit | Range | Resolution
FR_Power | Power[kW] | uint16 | % | 0~100 | 0.01
FR_Mode | FR Mode | uint16 | % | 0~500 | 1

## Sheet1
Delta_SOCv | Gain
1 | 0.0002
-1.5 | -0.0003
-2.2 | -0.0005
-3.2 | -0.002
-4 | -0.005
-5 | -0.02
Delta_SOCv | Gain
-1 | -0.0002 | -1
1.5 | 0.0003
2.2 | 0.0005
3.2 | 0.002
4 | 0.005
5 | 0.02